## Fault Behavior Mapping
Paper | Faults | Fault Mapping to FSBrick |  | FSBrick Entities | Count for FSBrick
Yan, 2018 | cooling coil tube fouling | Coil_Fouling (brick:Cooling_Coil) |  | Valve_Stuck | 16
| cooling coil dust on fins |  | no controlled vocab for this fault nature | Valve_Leakage | 8
| cooling coil valve stuck closed | Valve_Stuck (brick:Cooling_Coil) |  | Coil_Fouling | 9
| cooling coil valve stuck open | Valve_Stuck (brick:Cooling_Coil) |  | Damper_Stuck | 15
Qiu, 2020 | air valve stuck (of specific room) | Damper_Stuck (brick:Damper) |  | Damper_Leakage | 4
| water valve stuck | Valve_Stuck (brick:Water_Valve) |  | Damper_Malfunctioning | 2
| fan stuck | Fan_Stuck (brick:Fan) |  | Fan_Stuck | 5
| pump stuck | Pump_Stuck (brick:Pump) |  | Fan_Malfunctioning | 7
| pipe scaling | Coil_Fouling (brick:Coil) |  | Filter_Block | 3
Pradhan, 2021 | AHU outdoor air damper stuck higher than normal | Damper_Stuck (brick:Outside_Damper) |  | Air_Plenum_Block | 1
| AHU outdoor air damper stuck lower than normal | Damper_Stuck (brick:Outside_Damper) |  | Air_Plenum_Leakage | 3
| AHU cooling coil valve stuck higher than normal | Valve_Stuck (brick:Cooling_Coil) |  | Pump_Stuck | 3
| AHU cooling coil valve stuck lower than normal | Valve_Stuck (brick:Cooling_Coil) |  | Pump_Leakage | 2
| AHU return fan speed higher than normal | Fan_Malfunctioning (brick:Return_Fan)
| AHU return fan speed lower than normal | Fan_Malfunctioning (brick:Return_Fan)
| AHU return fan complete failure | Fan_Malfunctioning (brick:Return_Fan)
| AHU outdoor air damper leaking | Damper_Leakage (brick:Outside_Damper)
| AHU air loop supply duct leakage | Air_Plenum_Leakage (brick:Supply_Air_Plenum)
Zhao, 2017 | F4: Stuck OA damper | Damper_Stuck (brick:Outside_Damper)
| F5: Stuck RA damper | Damper_Stuck (brick:Return_Damper)
| F6: Stuck EA damper | Damper_Stuck (brick:Exhaust_Damper)
| F7: Stuck supply air fan | Fan_Stuck (brick:Supply_Fan)
| F8: Stuck return air fan | Fan_Stuck (brick:Return_Fan)
| F9: Leaking supply duct | Air_Plenum_Leakage (brick:Supply_Air_Plenum)
| F10: Filter fouling | Filter_Block (brick:Filter)
Zhao, 2015 | F11/F26: Stuck heating coil | Valve_Stuck (brick:Heating_Coil)
| F12: Leaking cooling coil valve | Valve_Leakage (brick:Cooling_Coil)
| F13: Heating coil fouling | Coil_Fouling (brick:Heating_Coil)
| F14: Pressure reduced on heating water circulating pump |  | pressure should be reduced by something; Therefore, this is a 'symptom' by our definition
| F21: Leaking heating coil valve | Valve_Leakage (brick:Heating_Coil)
| F22: Cooling coil fouling | Coil_Fouling (brick:Cooling_Coil)
| F23: Pressure reduced on chilled water circulating pump |  | pressure should be reduced by something; Therefore, this is a 'symptom' by our definition
| F28: Stuck cooling coil | Valve_Stuck (brick:Cooling_Coil)
Taal, 2020 | Supply fan broken | Fan_Malfunctioning (brick:Supply_Fan)
| Return fan broken | Fan_Malfunctioning (brick:Return_Fan)
| Damper is broken | Damper_Malfunctioning (brick:Damper)
| Bad filter | Filter_Block (brick:Filter)
| Leaking ducts | Air_Plenum_Leakage (brick:Air_Plenum)
| Clogged ducts | Air_Plenum_Block (brick:Air_Plenum)
| Stuck damper (room damper is broken) | Damper_Stuck (brick:Damper)
Yan, 2019 | EA damper stuck | Damper_Stuck (brick:Exhaust_Damper)
| Return fan stuck | Fan_Stuck (brick:Return_Fan)
| Cooling coil valve stuck | Valve_Stuck (brick:Cooling_Coil)
| Outdoor air damper stuck | Damper_Stuck (brick:Outside_Damper)
| OA damper leak | Damper_Leakage (brick:Outside_Damper)
| AHU duct leaking before supply fan |  | Duct is not a term in Brick
| AHU duct leaking after supply fan |  | Duct is not a term in Brick
| Air filter blocked | Filter_Block (brick:Filter)
| Mixed air damper unstable | Damper_Malfunctioning (brick:Mixed_Damper)
| Heating coil fouling | Coil_Fouling (brick:Heating_Coil)
| Heating coil reduced capacity |  | heating coil should have reduced capacity by something; Therefore, this is a 'symptom' by our definition
Li, 2021 | Condenser fouling | Coil_Fouling (brick:Condenser)
Excessive infiltration
Fan, 2024 | Exhaust air damper stuck | Damper_Stuck (brick:Exhaust_Damper)
| Outdoor air damper stuck | Damper_Stuck (brick:Outside_Damper)
| Cooling coil valve stuck | Valve_Stuck (brick:Cooling_Coil)
| Heating coil valve leakage | Valve_Leakage (brick:Heating_Coil)
| Return air fan fixed | Fan_Stuck (brick:Return_Fan)
| Return air fan total failure | Fan_Malfunctioning (brick:Return_Fan)
| Outdoor air damper stuck | Damper_Stuck (brick:Outside_Damper)
| Outdoor air damper leakage | Damper_Leakage (brick:Outside_Damper)
| Cooling coil valve stuck | Valve_Stuck (brick:Cooling_Coil)
| Cooling coil valve leakage | Valve_Leakage (brick:Cooling_Coil)
| Heating coil valve stuck | Valve_Stuck (brick:Heating_Coil)
| Heating coil valve leakage | Valve_Leakage (brick:Heating_Coil)
| Outdoor air damper stuck | Damper_Stuck (brick:Outside_Damper)
| Cooling coil valve stuck | Valve_Stuck (brick:Cooling_Coil)
| Heating coil valve stuck | Valve_Stuck (brick:Heating_Coil)
| Heating coil valve leakage | Valve_Leakage (brick:Heating_Coil)
Chen, 2023 | AHU duct leaking (after supply fan) |  | Duct is not a term in Brick
| AHU duct leaking (before supply fan) |  | Duct is not a term in Brick
| Cooling coil valve stuck | Valve_Stuck (brick:Cooling_Coil)
House, APAR | Leaking cooling coil valve | Valve_Leakage (brick:Cooling_Coil)
| Stuck cooling coil valve | Valve_Stuck (brick:Cooling_Coil)
| Fouled cooling coil | Coil_Fouling (brick:Cooling_Coil)
| Chilled water circulating pump fault | Pump_Stuck/Pump_Leakage (brick:Chilled_Water_Pump)
| Leaking heating coil valve | Valve_Leakage (brick:Heating_Coil)
| Stuck heating coil valve | Valve_Stuck (brick:Heating_Coil)
| Fouled heating coil | Coil_Fouling (brick:Heating_Coil)
| Hot water circulating pump fault | Pump_Stuck/Pump_Leakage (brick:Hot_Water_Pump)
| Leaking mixing box damper(s) | Damper_Leakage (brick:Mixed_Damper)
| Stuck mixing box damper(s) | Damper_Stuck (brick:Mixed_Damper)
Liang, 2007 | recirculation damper stuck | Damper_Stuck (brick:Return_Damper)
| cooling coil fouling | Coil_Fouling (brick:Cooling_Coil)
| cooling coil block |  | No such thing as coil block in our FSBrick entities
| supply fan speed decreasing | Fan_Malfunctioning (brick:Supply_Fan)
Count: | 86 | 76
Goodness-of-fit percentage: |  | 0.88235

## Fault Severity Mapping
| Faults | Severity | Fault Severity Mapping to FSBrick |  | FSBrick Entities | Count for FSBrick
Yan, 2018 | cooling coil tube fouling | decrease in tube diameter | hasSeverity; brick:Flow with value Literal |  | hasSeverity; brick:Flow with value Literal | 16
| cooling coil dust on fins | decrease in surface area |  |  | hasSeverity; brick:Position with value Literal | 38
| cooling coil valve stuck closed | 0% | hasSeverity; brick:Position with value Literal |  | hasSeverity; brick:Rotational_Speed with value Literal | 9
| cooling coil valve stuck open | 100% | hasSeverity; brick:Position with value Literal
Qiu, 2020 | air valve stuck (of specific room) | 80% open | hasSeverity; brick:Position with value Literal
water valve stuck
fan stuck
pump stuck
| pipe scaling | 75% | hasSeverity; brick:Flow with value Literal
Pradhan, 2021 | AHU outdoor air damper stuck higher than normal | 10% | hasSeverity; brick:Position with value Literal
|  | 0% | hasSeverity; brick:Position with value Literal
|  | 100% | hasSeverity; brick:Position with value Literal
|  | 15% | hasSeverity; brick:Position with value Literal
|  | 5% | hasSeverity; brick:Position with value Literal
AHU outdoor air damper stuck lower than normal
| AHU cooling coil valve stuck higher than normal | 0% (100% is in here too, but it is a duplicate of c5) | hasSeverity; brick:Position with value Literal
|  | 15% | hasSeverity; brick:Position with value Literal
|  | 5% | hasSeverity; brick:Position with value Literal
AHU cooling coil valve stuck lower than normal
AHU return fan speed higher than normal
AHU return fan speed lower than normal
AHU return fan complete failure
AHU outdoor air damper leaking
| AHU air loop supply duct leakage | 20% | hasSeverity; brickFlow with value Literal
Zhao, 2017 | Stuck OA damper | max position | hasSeverity; brick:Position with value Literal
|  | partially open | hasSeverity; brick:Position with value Literal
|  | min position | hasSeverity; brick:Position with value Literal
| Stuck RA damper | max position | hasSeverity; brick:Position with value Literal
|  | partially open | hasSeverity; brick:Position with value Literal
|  | min position | hasSeverity; brick:Position with value Literal
| Stuck EA damper | max position | hasSeverity; brick:Position with value Literal
|  | partially open | hasSeverity; brick:Position with value Literal
|  | min position | hasSeverity; brick:Position with value Literal
| Stuck supply air fan | max speed | hasSeverity; brick:Rotational_Speed with value Literal
|  | min speed | hasSeverity; brick:Rotational_Speed with value Literal
|  | partial speed | hasSeverity; brick:Rotational_Speed with value Literal
|  | complete failure |  | difficulty with qualitative descriptors
| Stuck return air fan | max speed | hasSeverity; brick:Rotational_Speed with value Literal
|  | min speed | hasSeverity; brick:Rotational_Speed with value Literal
|  | partial speed | hasSeverity; brick:Rotational_Speed with value Literal
|  | complete failure |  | difficulty with qualitative descriptors
| Leaking supply duct | heavily | hasSeverity; brick:Flow with value Literal
|  | slightly | hasSeverity; brick:Flow with value Literal
| Filter fouling | fouling | hasSeverity; brick:Flow with value Literal
|  | broken |  | difficulty with qualitative descriptors
Zhao, 2015 | Stuck heating coil | stuck at max | hasSeverity; brick:Position with value Literal
|  | positive |  | difficulty with qualitative descriptors
|  | negative |  | difficulty with qualitative descriptors
|  | stuck at min | hasSeverity; brick:Position with value Literal
| Leaking cooling coil valve | leaking heavily | hasSeverity; brick:Flow with value Literal
|  | leaking slightly | hasSeverity; brick:Flow with value Literal
Heating coil fouling
Pressure reduced on heating water circulating pump
| Leaking heating coil valve | leaking heavily | hasSeverity; brick:Flow with value Literal
|  | leaking slightly | hasSeverity; brick:Flow with value Literal
Cooling coil fouling
Pressure reduced on chilled water circulating pump
| Stuck cooling coil | stuck at max | hasSeverity; brick:Position with value Literal
|  | positive stuck |  | difficulty with qualitative descriptors
|  | negative stuck |  | difficulty with qualitative descriptors
|  | stuck at min | hasSeverity; brick:Position with value Literal
Taal, 2020 | Supply fan broken
Return fan broken
Damper is broken
Bad filter
Leaking ducts
Clogged ducts
Stuck damper (room damper is broken)
Yan, 2019 | EA damper stuck | fully open | hasSeverity; brick:Position with value Literal
|  | fully closed | hasSeverity; brick:Position with value Literal
|  | 40% open | hasSeverity; brick:Position with value Literal
| Return fan stuck | 30% speed | hasSeverity; brick:Rotational_Speed with value Literal
|  | 20% speed | hasSeverity; brick:Rotational_Speed with value Literal
|  | 80% speed | hasSeverity; brick:Rotational_Speed with value Literal
|  | complete failure |  | difficulty with qualitative descriptors
| Cooling coil valve stuck | fully closed | hasSeverity; brick:Position with value Literal
|  | fully open | hasSeverity; brick:Position with value Literal
|  | 15% partially open | hasSeverity; brick:Position with value Literal
|  | 65% partially open | hasSeverity; brick:Position with value Literal
|  | 50% partially open | hasSeverity; brick:Position with value Literal
| Outdoor air damper stuck | fully closed | hasSeverity; brick:Position with value Literal
| OA damper leak | 55% open | hasSeverity; brick:Position with value Literal
|  | fully closed | hasSeverity; brick:Position with value Literal
AHU duct leaking before supply fan
AHU duct leaking after supply fan
| Air filter blocked | 10% of area | hasSeverity; brick:Flow with value Literal
|  | 25% of area | hasSeverity; brick:Flow with value Literal
Mixed air damper unstable
| OA damper stuck | fully closed | hasSeverity; brick:Position with value Literal
| OA damper leaking | 52% open | hasSeverity; brick:Position with value Literal
|  | 62% open | hasSeverity; brick:Position with value Literal
| Heating coil fouling | stage 1 | hasSeverity; brick:Flow with value Literal
|  | stage 2 | hasSeverity; brick:Flow with value Literal
| Heating coil reduced capacity | stage 1 | hasSeverity; brick:Flow with value Literal
|  | stage 2 | hasSeverity; brick:Flow with value Literal
|  | stage 3 | hasSeverity; brick:Flow with value Literal
Li, 2021 | Condenser fouling | 25% reduction in condenser coil air flow full load | hasSeverity; brick:Flow with value Literal
|  | 50% reduction in condenser coil air flow full load | hasSeverity; brick:Flow with value Literal
| Excessive infiltration | +' 20% infiltration | hasSeverity; brick:Flow with value Literal
|  | +' 40% infiltration | hasSeverity; brick:Flow with value Literal
Fan, 2024 | Exhaust air damper stuck | at fully open | hasSeverity; brick:Position with value Literal
|  | at 40% | hasSeverity; brick:Position with value Literal
|  | at fully closed | hasSeverity; brick:Position with value Literal
| Outdoor air damper stuck | at 55% | hasSeverity; brick:Position with value Literal
|  | at 45% | hasSeverity; brick:Position with value Literal
|  | at fully closed | hasSeverity; brick:Position with value Literal
| Cooling coil valve stuck | at fully open | hasSeverity; brick:Position with value Literal
|  | at 50% | hasSeverity; brick:Position with value Literal
|  | at fully closed | hasSeverity; brick:Position with value Literal
| Heating coil valve leakage | at 2.0 GPM | hasSeverity; brick:Flow with value Literal
|  | at 1.0 GPM | hasSeverity; brick:Flow with value Literal
|  | at 0.4 GPM | hasSeverity; brick:Flow with value Literal
| Return air fan fixed | at 80% speed | hasSeverity; brick:Rotational_Speed with value Literal
|  | at 30% speed | hasSeverity; brick:Rotational_Speed with value Literal
Return air fan total failure
| Outdoor air damper stuck | at fully open | hasSeverity; brick:Position with value Literal
|  | at 50% | hasSeverity; brick:Position with value Literal
| Outdoor air damper leakage | at 50% | hasSeverity; brick:Flow with value Literal
|  | at 20% | hasSeverity; brick:Flow with value Literal
| Cooling coil valve stuck | at fully open | hasSeverity; brick:Position with value Literal
|  | at 50% | hasSeverity; brick:Position with value Literal
|  | at fully closed | hasSeverity; brick:Position with value Literal
| Cooling coil valve leakage | at 50% | hasSeverity; brick:Flow with value Literal
|  | at 5% | hasSeverity; brick:Flow with value Literal
| Heating coil valve stuck | at fully open | hasSeverity; brick:Position with value Literal
|  | at 50% | hasSeverity; brick:Position with value Literal
|  | at fully closed | hasSeverity; brick:Position with value Literal
| Heating coil valve leakage | at 40% | hasSeverity; brick:Flow with value Literal
|  | at 5% | hasSeverity; brick:Flow with value Literal
| Outdoor air damper stuck | at fully open | hasSeverity; brick:Position with value Literal
|  | at fully closed | hasSeverity; brick:Position with value Literal
| Cooling coil valve stuck | at fully open | hasSeverity; brick:Position with value Literal
| Heating coil valve stuck | at fully open | hasSeverity; brick:Position with value Literal
|  | at 50% | hasSeverity; brick:Position with value Literal
| Heating coil valve leakage | at 40% | hasSeverity; brick:Flow with value Literal
Chen, 2023 | AHU duct leaking (after supply fan)
AHU duct leaking (before supply fan)
| Cooling coil valve stuck | 15% open | hasSeverity; brick:Position with value Literal
|  | 65% open | hasSeverity; brick:Position with value Literal
Liang, 2007 | recirculation damper stuck | 30% | hasSeverity; brick:Position with value Literal
|  | 35% | hasSeverity; brick:Position with value Literal
|  | 40% | hasSeverity; brick:Position with value Literal
| cooling coil fouling | 15% | hasSeverity; brick:Flow with value Literal
|  | 20% | hasSeverity; brick:Flow with value Literal
|  | 25% | hasSeverity; brick:Flow with value Literal
| cooling coil block | 30% | hasSeverity; brick:Flow with value Literal
|  | 40% | hasSeverity; brick:Flow with value Literal
|  | 50% | hasSeverity; brick:Flow with value Literal
| supply fan speed decreasing | 10% | hasSeverity; brick:Rotational_Speed with value Literal
|  | 12.5% | hasSeverity; brick:Rotational_Speed with value Literal
|  | 15% | hasSeverity; brick:Rotational_Speed with value Literal
COUNT: |  | 125 | 116
Goodness-of-fit percentage: |  | 0.928

## Symptom Mapping
Paper | Symptoms | Symptom Mapping to FSBrick | Alarm | **Most specific alarms were applied if they could be found
Yan, 2018 | outdoor air temperature | hasSymptom; brick:Air_Temperature_Alarm; (brick:Outside_Air) | TRUE
| supply air temperature | hasSymptom; brick:Supply_Air_Temperature_Alarm | TRUE
| return air temperature | hasSymptom; brick:Return_Air_Temperature_Alarm | TRUE
| outdoor air humidity | hasSymptom; brick:Humidity_Alarm; (brick:Outside_Air) | TRUE
| supply air humidity | hasSymptom; brick:Humidity_Alarm; (brick:Supply_Air) | TRUE
| return air humidity | hasSymptom; brick:Humidity_Alarm; (brick:Return_Air) | TRUE
| outdoor air mass flow rate | hasSymptom; brick:Air_Flow_Alarm; (brick:Outside_Air) | TRUE
| supply air mass flow rate | hasSymptom; brick:Air_Flow_Alarm; (brick:Supply_Air) | TRUE
| return air mass flow rate | hasSymptom; brick:Air_Flow_Alarm; (brick: Return_Air) | TRUE
| chilled water temperature | hasSymptom; brick:Water_Temperature_Alarm; (brick:Chilled_Water) | TRUE
| chilled water mass flow rate | (brick:Chilled_Water) | FALSE
| supply fan power consumption | hasSymptom; brick:Power_Alarm; (brick:Supply_Fan) | TRUE
| return fan power consumption | hasSymptom; brick:Power_Alarm; (brick:Return_Fan) | TRUE
Qiu, 2020 | low room air temperature (&increased fan energy consumption, increased water pump energy consumption) | hasSymptom; brick:Air_Temperature_Alarm; (brick:Zone_Air) | TRUE
| increased fan energy consumption | hasSymptom; brick:Power_Alarm; (brick:Fan) | TRUE
| increased water pump energy consumption | hasSymptom; brick:Power_Alarm; (brick:Water_Pump) | TRUE
FALSE
| supply air temperature alarm (increased fan energy consumption, increased water pump energy consumption) | hasSymptom; brick:Supply_Air_Temperature_Alarm | TRUE
Zhao, 2017 | E1: Difference between supply air pressure and its set point (positive) | hasSymptom; brick:Pressure_Alarm; (brick:Supply_Air) | TRUE
| E1: Difference between supply air pressure and its set point (negative) | hasSymptom; brick:Pressure_Alarm; (brick:Supply_Air) | TRUE
| E2: Supply fan power consumption is a polynomial function of supply air flow rate (extremely positive) | hasSymptom; brick:Power_Alarm; (brick:Supply_Fan) | FALSE
| E2: Supply fan power consumption is a polynomial function of supply air flow rate (positive) | hasSymptom; brick:Power_Alarm; (brick:Supply_Fan) | FALSE
| E2: Supply fan power consumption is a polynomial function of supply air flow rate (negative) | hasSymptom; brick:Power_Alarm; (brick:Supply_Fan) | FALSE
| E3: Return fan power consumption is a polynomial function of return fan speed (positive) | hasSymptom; brick:Power_Alarm; (brick:Return_Fan) | FALSE
| E3: Return fan power consumption is a polynomial function of return fan speed (negative) | hasSymptom; brick:Power_Alarm; (brick:Return_Fan) | FALSE
| E4: Pressure drop across a filter is a polynomial function of supply air flow rate (positive) | hasSymptom; brick:Pressure_Alarm; (brick:Filter) | FALSE
| E4: Pressure drop across a filter is a polynomial function of supply air flow rate (negative) | hasSymptom; brick:Pressure_Alarm; (brick:Filter) | FALSE
| E4: Pressure drop across a filter is a polynomial function of supply air flow rate (zero) | hasSymptom; brick:Pressure_Alarm; (brick:Filter) | FALSE
| E5: Supply fan control signal (max value) |  | FALSE
| E5: Supply fan control signal (min value) |  | FALSE
| E9: Difference between return air and mixed air temperatures (negative) | hasSymptom; brick:Air_Temperature_Alarm; | FALSE
| E9: Difference between return air and mixed air temperatures (positive) | hasSymptom; brick:Air_Temperature_Alarm; | FALSE
| E10: Difference between outdoor air and mixed air temperatures (negative) | hasSymptom; brick:Air_Temperature_Alarm; | FALSE
| E10: Difference between outdoor air and mixed air temperatures (positive) | hasSymptom; brick:Air_Temperature_Alarm; | FALSE
| E11: Supply fan power measurement (max value) | hasSymptom; brick:Power_Alarm; (brick:Supply_Fan) | TRUE
| E11: Supply fan power measurement (min value) | hasSymptom; brick:Power_Alarm; (brick:Supply_Fan) | TRUE
| E11: Supply fan power measurement (partial value) | hasSymptom; brick:Power_Alarm; (brick:Supply_Fan) | TRUE
| E11: Supply fan power measurement (zero) | hasSymptom; brick:Power_Alarm; (brick:Supply_Fan) | TRUE
Zhao, 2015 | E12: Supply air temperature is too low | hasSymptom; brick:Supply_Air_Temperature_Alarm | TRUE
| E18: Cooling coil control signal open valve | hasSymptom; brick:Valve_Position_Alarm; (brick:Cooling_Valve) | TRUE
| E18: Cooling coil control signal close valve | hasSymptom; brick:Valve_Position_Alarm; (brick:Cooling_Valve) | TRUE
| E42: Predicted control signal of heating coil valve vs actual value (positive max) | hasSymptom; brick:Valve_Position_Alarm; (brick:Heating_Valve) | TRUE
| E42: Predicted control signal of heating coil valve vs actual value (positive) | hasSymptom; brick:Valve_Position_Alarm; (brick:Heating_Valve) | TRUE
| E42: Predicted control signal of heating coil valve vs actual value (negative) | hasSymptom; brick:Valve_Position_Alarm; (brick:Heating_Valve) | TRUE
| E42: Predicted control signal of heating coil valve vs actual value (negative min) | hasSymptom; brick:Valve_Position_Alarm; (brick:Heating_Valve) | TRUE
| E13: Status of chilled water circulating pump (closed) | (brick:Chilled_Water_Pump) brick:Position_Alarm | TRUE
| E14: Reduced pressure of pressure difference of the supply heating water loop | hasSymptom; brick:Pressure_Alarm; (brick:Hot_Water_Pump) | TRUE
| E15: Low temperature of supply heating water | hasSymptom; brick:Water_Temperature_Alarm; (brick:Supply_Hot_Water) | TRUE
| E44: R7 in APAR Positive | (brick:Supply_Air_Temperature) | FALSE
| E44: R7 in APAR negative | (brick:Supply_Air_Temperature) | FALSE
| E33: Supply air temperature outside of threshold (lo) | hasSymptom; brick:Supply_Air_Temperature_Alarm | TRUE
| E37: Supply air temperature outside of threshold (hi) | hasSymptom; brick:Supply_Air_Temperature_Alarm | TRUE
| E19: R1 in APAR |  | FALSE
| E20: R27 in APAR |  | FALSE
| E21: R2 and R18 in APAR |  | FALSE
| E23: R26 in APAR |  | FALSE
| E28: R6, R12, and R17 in APAR |  | FALSE
| E29: Pressure difference of the cooling water loop (pressure reduced) | hasSymptom; brick:Pressure_Alarm; (brick:Chilled_Water_Loop) | TRUE
| E31: R12 in APAR |  | FALSE
| E32: R8 in APAR |  | FALSE
| E35: R11 and R16 in APAR |  | FALSE
| E36: R10 in APAR |  | FALSE
| E38: Heating coil control signal (open valve) | hasSymptom; brick:Valve_Position_Alarm; (brick:Heating_Valve) | TRUE
| E38: Heating coil control signal (closed valve) | hasSymptom; brick:Valve_Position_Alarm; (brick:Heating_Valve) | TRUE
| E27: Closed heating water circulating pump | (brick:Hot_Water_Pump); brick:Position_Alarm | TRUE
| E37: Supply air temperature too high | hasSymptom; brick:Supply_Air_Temperature_Alarm | TRUE
| E43: Predicted control signal of cooling coil valve vs actual value (positive max) | hasSymptom; brick:Valve_Position_Alarm; (brick:Cooling_Valve) | TRUE
| E43: Predicted control signal of cooling coil valve vs actual value (positive) | hasSymptom; brick:Valve_Position_Alarm; (brick:Cooling_Valve) | TRUE
| E43: Predicted control signal of cooling coil valve vs actual value (negative) | hasSymptom; brick:Valve_Position_Alarm; (brick:Cooling_Valve) | TRUE
| E43: Predicted control signal of cooling coil valve vs actual value (negative min) | hasSymptom; brick:Valve_Position_Alarm; (brick:Cooling_Valve) | TRUE
| E34: High supply chilled water temperature | hasSymptom; brick:Water_Temperature_Alarm (brick:Supply_Chilled_Water) | TRUE
Taal, 2020 | AHU flow rate = 0 (AHU flow rate = 0 OR flow rate = 0 and occupied OR High CO2 and flow rate = 0) | hasSymptom; brick:Air_Flow_Alarm; (brick:AHU) | TRUE
| CO2 (High CO2 and flow rate = 0 OR High CO2 and low flow rate OR low CO2 and non zero flow rate; occupied but flow rate is zero) | hasSymptom; brick:CO2_Alarm; (brick:AHU) | TRUE
Yan, 2019 | Energy Consumption of cooling coil | hasSymptom; brick:Power_Alarm; (brick:Cooling_Coil) | TRUE
| Energy consumption of heating coil | hasSymptom; brick:Power_Alarm; (brick:Heating_Coil) | TRUE
| Supply air temperature | hasSymptom; brick:Supply_Air_Temperature_Alarm | TRUE
| Return air temperature | hasSymptom; brick:Return_Air_Temperature_Alarm | TRUE
| Supply air relative humidity | hasSymptom; brick:Humidity_Alarm; (brick:Supply_Air) | TRUE
Li, 2021 | Measured RTU supply air temperature | hasSymptom; brick:Supply_Air_Temperature_Alarm; (brick:RTU) | TRUE
| Measured RTU return air temperature | hasSymptom; brick:Return_Air_Temperature_Alarm; (brick:RTU) | TRUE
| Measured ambient temperature in each room | hasSymptom; brick:Air_Temperature_Alarm; (brick:Zone_Air) | TRUE
| VAV box supply air temperature for each room | hasSymptom; brick:Air_Temperature_Alarm; (brick:Zone_Air) | TRUE
| Measured ambient relative humidity in each room | hasSymptom; brick:Humidity_Alarm; (brick:Zone_Air) | TRUE
| Measured RTU volumetric air flow rate | hasSymptom; brick:Air_Flow_Alarm; (brick:RTU) | TRUE
| RTU electricity consumption | hasSymptom; brick:Power_Alarm; (brick:RTU) | TRUE
| Total electricity consumption of HVAC system | hasSymptom; brick:Power_Alarm; (brick:HVAC_System) | TRUE
| Total electricity consumption of lighting system | hasSymptom; brick:Power_Alarm; (brick:Lighting_System) | TRUE
| RTU supply air fan electricity consumption | hasSymptom; brick:Power_Alarm; (brick:Supply_Fan, brick:RTU) | TRUE
| RTU compressor status; 0 - off, 1 - on | hasSymptom; brick:Alarm; (brick:Compressor, brick:On_Off_Status) | TRUE
| Control command of lighting system; 0 - off, 1 - on | hasSymptom; brick:Alarm; (brick:Lighting_System, brick:On_Off_Status) | TRUE
| VAV box reheat status for each room; 0 - off, 1 - on | hasSymptom; brick:Alarm; (brick:Variable_Air_Volume_Box_With_Reheat, brick:On_Off_Status) | TRUE
Fan, 2024 | AHU: Supply Air Temperature | hasSymptom; brick:Supply_Air_Temperature_Alarm; (brick:AHU) | TRUE
(For MZVAV) | AHU: Supply Air Temperature Set Point | hasSymptom; brick:Supply_Air_Temperature_Alarm; (brick:AHU) | TRUE
| AHU: Outdoor Air Temperature | hasSymptom; brick:Air_Temperature_Alarm; (brick:Outside_Air) | TRUE
| AHU: Mixed Air Temperature | hasSymptom; brick:Air_Temperature_Alarm; (brick:Mixed_Air) | TRUE
| AHU: Return Air Temperature | hasSymptom; brick:Return_Air_Temperature_Alarm; (brick:AHU) | TRUE
| AHU: Supply Air Fan Status | hasSymptom; brick:Alarm; (brick:Supply_Fan, brick:Fan_Status) | TRUE
| AHU: Return Air Fan Status | hasSymptom; brick:Alarm; (brick:Return_Fan, brick:Fan_Status) | TRUE
| AHU: Supply Air Fan Speed Control Signal | hasSymptom; brick:Alarm; (brick:Supply_Fan, brick:Speed_Status) | TRUE
| AHU: Return Air Fan Speed Control Signal | hasSymptom; brick:Alarm; (brick:Return_Fan, brick:Speed_Status) | TRUE
| AHU: Outdoor Air Damper Control Signal | hasSymptom; brick:Alarm; (brick:Outside_Damper, brick:Damper_Position_Status) | TRUE
| AHU: Return Air Damper Control Signal | hasSymptom; brick:Alarm; (brick:Return_Damper, brick:Damper_Position_Status) | TRUE
| AHU: Cooling Coil Valve Control Signal | hasSymptom; brick:Valve_Position_Alarm (brick:Cooling_Valve) | TRUE
| AHU: Heating Coil Valve Control Signal | hasSymptom; brick:Valve_Position_Alarm (brick:Heating_Valve) | TRUE
| AHU: Supply Air Duct Static Pressure | hasSymptom; brick:Pressure_Alarm; (brick:Supply_Air_Duct_Pressure_Status) | TRUE
| AHU: Supply Air Duct Static Pressure Set Point | hasSymptom; brick:Pressure_Alarm; (brick:Supply_Air_Duct_Pressure_Status) | TRUE
| Occupancy Mode Indicator | hasSymptom; brick:Alarm; (brick:Occupancy_Status) | TRUE
(For SZCAV) | AHU: Supply Air Temperature | hasSymptom; brick:Supply_Air_Temperature_Alarm; (brick:AHU) | TRUE
| AHU: Supply Air Temperature Heating Set Point | hasSymptom; brick:Supply_Air_Temperature_Alarm; (brick:AHU) | TRUE
| AHU: Supply Air Temperature Cooling Set Point | hasSymptom; brick:Supply_Air_Temperature_Alarm; (brick:AHU) | TRUE
| AHU: Outdoor Air Temperature | hasSymptom; brick:Air_Temperature_Alarm; (brick:Outside_Air) | TRUE
| AHU: Mixed Air Temperature | hasSymptom; brick:Air_Temperature_Alarm; (brick:Mixed_Air) | TRUE
| AHU: Return Air Temperature | hasSymptom; brick:Return_Air_Temperature_Alarm; (brick:AHU) | TRUE
| AHU: Supply Air Fan Status | hasSymptom; brick:Alarm; (brick:Supply_Fan, brick:Fan_Status) | TRUE
| AHU: Supply Air Fan Speed Control Signal | hasSymptom; brick:Alarm; (brick:Supply_Fan, brick:Speed_Status) | TRUE
| AHU: Exhaust Air Damper Control Signal | hasSymptom; brick:Alarm; (brick:Exhaust_Damper, brick:Damper_Position_Status) | TRUE
| AHU: Outdoor Air Damper Control Signal | hasSymptom; brick:Alarm; (brick:Outside_Damper, brick:Damper_Position_Status) | TRUE
| AHU: Return Air Damper Control Signal | hasSymptom; brick:Alarm; (brick:Return_Damper, brick:Damper_Position_Status) | TRUE
| AHU: Cooling Coil Valve Control Signal | hasSymptom; brick:Valve_Position_Alarm (brick:Cooling_Valve) | TRUE
| Occupancy Mode indicator | hasSymptom; brick:Alarm; (brick:Occupancy_Status) | TRUE
Chen, 2023 | Supplied air flow rates | hasSymptom; brick:Air_Flow_Alarm (brick:Supply_Air) | TRUE
| Return air flow rates | hasSymptom; brick:Air_Flow_Alarm (brick:Return_Air) | TRUE
| Supply fan power | hasSymptom; brick:Power_Alarm (brick:Supply_Fan) | TRUE
| Return fan power | hasSymptom; brick:Power_Alarm (brick:Return_Fan) | TRUE
| Differential pressure of supply fan |  | FALSE | No brick entity: differential pressure
| Differential pressure of return fan |  | FALSE | No brick entity: differential pressure
| Cooling coil valve position | hasSymptom; brick:Valve_Position_Alarm (brick:Cooling_Valve) | TRUE
| Heating coil valve position | hasSymptom; brick:Valve_Position_Alarm (brick:Heating_Valve) | TRUE
House, APAR | Rule 1: Comparison between supply air temperature, mixed air temperature, temperature rise across the supply fan, and temperature threshold |  | FALSE
| Rule 2: Comparison between return air temperature, outdoor air temperature, and minimum temperature threshold, with outdoor air fraction and minimum outdoor air fraction, and threshold for airflows |  | FALSE
| Rule 3: heating coil valve control signal compared against treshold for heating coil valve control signal AND supply air temperature, supply air temperature setpoint, and temperature threshold |  | FALSE
| Rule 4: heating coil valve control signal compared against treshold for heating coil valve control signal | hasSymptom; brick:Valve_Position_Alarm (brick:Heating_Valve) | TRUE
| Rule 5: outdoor air temperature compared against supply air temperature setpoint, temperature rise across the supply fan, and temperature threshold |  | FALSE
| Rule 6: supply air temperature compared against return air temperature, temperature rise across the return fan, and temperature threshold |  | FALSE
| Rule 7: supply air temperature, temperature rise across the supply fan, and mixed air temperature compared against temperature threshold |  | FALSE
| Rule 8: outdoor air temperature compared against supply air temperature setpoint, temperature rise across supply fan, and temperature threshold |  | FALSE
| Rule 9: Outdoor air temperature compared against changover air temperature for switching between modes 3 and 4 and temperature threshold |  | FALSE
| Rule 10: Outdoor air temperature and mixed air temperature compared against the temperature threshold |  | FALSE
| Rule 11: Supply air temperature compared against mixed air temperature, temperature rise across supply fan, and temperature threshold |  | FALSE
| Rule 12: Supply air temperature compared against return air temperature, temperature rise across return fan, and temperature threshold |  | FALSE
| Rule 13: heating coil valve control signal compared against treshold for heating coil valve control signal AND Supply air temperature and supply air temperature setpoint compared against temperature threshold |  | FALSE
| Rule 14: Cooling coil valve control signal compared against threshold parameter for cooling coil valve control signal | hasSymptom; brick:Valve_Position_Alarm (brick:Cooling_Valve) | TRUE
| Rule 15: Outdoor air temperature compared against changeover air temperature for switching between modes 3 and 4 and temperature threshold |  | FALSE
| Rule 16: Supply air temperature compared against mixed air temperature, temperature rise across supply fan, and temperature threshold |  | FALSE
| Rule 17: Supply air temperature compared against return air temperature, temperature rise across return fan, and temperature threshold |  | FALSE
| Rule 18: Return air temperature and outdoor air temperature compared against threshold on the min temperature diff between return and outdoor air AND outdoor air fraction and threshold on the minimum outdoor air fraction is compared against threshold parameter for airflows |  | FALSE
| Rule 19: cooling coil valve control signal compared against threshold for cooling coil valve control signal AND supply air temperature and supply air temperature setpoint compared against the temperature threshold |  | FALSE
| Rule 20: Cooling coil valve control signal compared against threshold for cooling coil valve control signal | hasSymptom; brick:Valve_Position_Alarm (brick:Cooling_Valve) | TRUE
| Rule 21: Cooling coil valve control signal compared to threshold for cooling coil valve control signal AND heating coil valve control signal compared to threshold for heating coil valve control signal AND threshold parameter associated with the mixing box damper control signal compared to mixing box damper control signal |  | FALSE
| Rule 22: Heating coil valve control signal compared against threshold for heating coil valve control signal AND cooling coil valve control signal compared to threshold for cooling coil valve control signal |  | FALSE
| Rule 23: Heating coil valve control signal compared against threshold for heating coil valve control signal AND mixing box damper control signal compared to threshold for mixing box damper control signal |  | FALSE
| Rule 24: threshold for mixing box damper control signal compared against mixing box damper control signal AND cooling coil valve control signal compared to threshold for cooling coil valve signal |  | FALSE
| Rule 25: Supply air temperature and supply air temperature setpoint compared against temperature threshold | hasSymptom; brick:Supply_Air_Temperature_Alarm | TRUE
| Rule 26: Mixed air temperature compared against the minimum of return air temperature and outdoor air temperature subtracted by temperature threshold |  | FALSE
| Rule 27: Mixed air temperature compared against the maximum of return air temperature and outdor air temperature added by temperature threshold |  | FALSE
| Rule 28: Number of mode transitions per hour should be greater than the max allowable number of mode transitions per hour | hasSymptom; brick:Cycle_Alarm | TRUE
Liang, 2007 | Mixed air temperature residual | hasSymptom; brick:Air_Temperature_Alarm; (brick:Mixed_Air) | TRUE
| Outlet water temperature residual | hasSymptom; brick:Water_Temperature_Alarm; (brick:Leaving_Water) | TRUE
| Supply air temperature residual | hasSymptom; brick:Supply_Air_Temperature_Alarm | TRUE
| Valve control signal residual | hasSymptom; brick:Valve_Position_Alarm | TRUE
COUNT: | 159 |  | 108
Goodness-of-fit percentage: |  |  | 0.67925
without symptoms that require multiple system variables | 129 |  | 103
0.79845

## Grouped Symptom Mapping
Paper | Fault | Grouped Symptoms | Symptom Mapping to FSBrick
House, APAR | Leaking cooling coil valve | Rules 1, 3, 4, 7 | fsbrick:Grouped_Symptom and fsbrick:hasSymptom | If symptoms (rules) could be represented
| Stuck cooling coil valve | Rules 1, 3, 4, 7, 11, 12, 13, 14, 16, 17, 19, 20 | fsbrick:Grouped_Symptom and fsbrick:hasSymptom | If symptoms (rules) could be represented
| Fouled cooling coil | Rules 12, 13, 14, 17, 19, 20 | fsbrick:Grouped_Symptom and fsbrick:hasSymptom | If symptoms (rules) could be represented
| Chilled water circulating pump fault | Rules 11, 12, 13, 14, 16, 17, 19, 20 | fsbrick:Grouped_Symptom and fsbrick:hasSymptom | If symptoms (rules) could be represented
| Leaking heating coil valve | Rules 7, 8, 11, 12, 13, 14, 16, 17, 19, 20 | fsbrick:Grouped_Symptom and fsbrick:hasSymptom | If symptoms (rules) could be represented
| Stuck heating coil valve | Rules 1, 3, 4, 7, 8, 11, 12, 13, 14, 16, 17, 19, 20 | fsbrick:Grouped_Symptom and fsbrick:hasSymptom | If symptoms (rules) could be represented
| Fouled heating coil | Rules 3, 4 | fsbrick:Grouped_Symptom and fsbrick:hasSymptom | If symptoms (rules) could be represented
| Hot water circulating pump fault | Rules 1, 3, 4 | fsbrick:Grouped_Symptom and fsbrick:hasSymptom | If symptoms (rules) could be represented
| Leaking mixing box damper(s) | Rules 2, 8, 10, 18 | fsbrick:Grouped_Symptom and fsbrick:hasSymptom | If symptoms (rules) could be represented
| Stuck mixing box damper(s) | Rules 2, 8, 10, 18 | fsbrick:Grouped_Symptom and fsbrick:hasSymptom | If symptoms (rules) could be represented
Taal, 2020 | AHU broken | High Co2 AND air flow rate = 0 | fsbrick:Grouped_Symptom and fsbrick:hasSymptom
| Damper stuck | High CO2 AND air flow rate = 0 | fsbrick:Grouped_Symptom and fsbrick:hasSymptom
|  | High CO2 and low air flow rate | fsbrick:Grouped_Symptom and fsbrick:hasSymptom
|  | Low CO2 and air flow rate > 0 | fsbrick:Grouped_Symptom and fsbrick:hasSymptom
Zhao, 2015 | Cooling coil valve stuck (fully open) | E12, E42 | fsbrick:Grouped_Symptom and fsbrick:hasSymptom
Zhao, 2017 | Return fan at fixed speed (30%) | E1 (2%), E2 (37%), E3 (100%) | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| Return fan complete failure | E2 (67%), E3 (100%) | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| Outdoor air damper stuck (fully closed) | E1 (5%), E2 (99%), E3 (4%) | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| Outside air damper stuck (fully closed) | E1 (100%), E2 (100%) | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| Outside air damper stuck (fully closed) | E1 (100%), E2 (100%) | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| Exhaust air damper (fully closed) | E2 (1%), E3 (100%) | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| Outside air damper stuck (fully closed) | E1 (100%), E2 (100%), E3 (51%) | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| Outside air damper stuck (40% open) | E1 (97%), E2 (100%), E3 (44%) | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
Liang, 2007 | recirculation damper stuck | Mixed air temperature alarm AND Outlet water temperature alarm | fsbrick:Grouped_Symptom and fsbrick:hasSymptom
| supply fan speed decreasing | Supply air temperature AND Outlet water temperature alarm | fsbrick:Grouped_Symptom and fsbrick:hasSymptom
COUNT: |  | 25 | 25
Goodness-of-fit percentage: |  | 100%

## Probability for FSR Mapping
Paper | Fault | Symptoms | Symptom Probability | Symptom Mapping to FSBrick
Pradhan, 2021 | AHU outdoor air damper stuck higher than normal (10%) | All system variables | 2% | fsbrick:hasSymptomProb
| AHU outdoor air damper stuck higher than normal (0%) | All system variables | 85% | fsbrick:hasSymptomProb
| AHU outdoor air damper stuck higher than normal (100%) | All system variables | 71% | fsbrick:hasSymptomProb
| AHU outdoor air damper stuck higher than normal (15%) | All system variables | 71% | fsbrick:hasSymptomProb
| AHU outdoor air damper stuck higher than normal (5%) | All system variables | 82% | fsbrick:hasSymptomProb
| AHU cooling coil valve stuck higher than normal (0%) | All system variables | 87% | fsbrick:hasSymptomProb
| AHU cooling coil valve stuck higher than normal (15%) | All system variables | 89% | fsbrick:hasSymptomProb
| AHU cooling coil valve stuck higher than normal (5%) | All system variables | 88% | fsbrick:hasSymptomProb
| AHU cooling coil valve stuck higher than normal (100%) | All system variables | 63% | fsbrick:hasSymptomProb
| AHU air loop supply duct leakage (20%) | All system variables | 90% | fsbrick:hasSymptomProb
Zhao, 2015 | Cooling coil valve stuck (fully open) | E12, E42 | 28% | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| Cooling coil valve stuck (20% open) | E42 | 27% | fsbrick:hasSymptomProb
| Heating coil reduced capacity 1 | E42 | 99% | fsbrick:hasSymptomProb
| Heating coil reduced capacity 2 | E42 | 99% | fsbrick:hasSymptomProb
| Heating coil reduced capacity 3 | E42 | 97% | fsbrick:hasSymptomProb
| Cooling coil valve stuck (fully closed) | E12 | 67% | fsbrick:hasSymptomProb
| Cooling coil valve stuck (fully open) | E43 | 100% | fsbrick:hasSymptomProb
| Cooling coil valve stuck (partially open - 50%) | E43 | 100% | fsbrick:hasSymptomProb
Zhao, 2017 | Return fan at fixed speed (30%) | E1 (2%), E2 (37%), E3 (100%) | 57% | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| Return fan complete failure | E2 (67%), E3 (100%) | 100% | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| Outdoor air damper stuck (fully closed) | E1 (5%), E2 (99%), E3 (4%) | 99% | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| AHU duct leaking (before supply fan) | E2 (90%) | 54% | fsbrick:hasSymptomProb
| AHU duct leaking (before supply fan) | E2 (79%) | 56% | fsbrick:hasSymptomProb
| Outside air damper stuck (fully closed) | E1 (100%), E2 (100%) | 79% | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| Outside air damper stuck (fully closed) | E1 (100%), E2 (100%) | 78% | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| Exhaust air damper (fully closed) | E2 (1%), E3 (100%) | 50% | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| Outside air damper stuck (fully closed) | E1 (100%), E2 (100%), E3 (51%) | 98% | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| Outside air damper stuck (40% open) | E1 (97%), E2 (100%), E3 (44%) | 93% | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| Return fan complete failure | E3 (100%) | 100% | fsbrick:hasSymptomProb
COUNT: |  | 29 | 29
Goodness-of-fit percentage: |  | 100%

## FSR Mapping
Paper | Fault | Grouped Symptoms | Grouped Symptom Probability | Symptom Mapping to FSBrick
House, APAR | Leaking cooling coil valve | Rules 1, 3, 4, 7 |  | fsbrick:Grouped_Symptom and fsbrick:hasSymptom
| Stuck cooling coil valve | Rules 1, 3, 4, 7, 11, 12, 13, 14, 16, 17, 19, 20 |  | fsbrick:Grouped_Symptom and fsbrick:hasSymptom
| Fouled cooling coil | Rules 12, 13, 14, 17, 19, 20 |  | fsbrick:Grouped_Symptom and fsbrick:hasSymptom
| Chilled water circulating pump fault | Rules 11, 12, 13, 14, 16, 17, 19, 20 |  | fsbrick:Grouped_Symptom and fsbrick:hasSymptom
| Leaking heating coil valve | Rules 7, 8, 11, 12, 13, 14, 16, 17, 19, 20 |  | fsbrick:Grouped_Symptom and fsbrick:hasSymptom
| Stuck heating coil valve | Rules 1, 3, 4, 7, 8, 11, 12, 13, 14, 16, 17, 19, 20 |  | fsbrick:Grouped_Symptom and fsbrick:hasSymptom
| Fouled heating coil | Rules 3, 4 |  | fsbrick:Grouped_Symptom and fsbrick:hasSymptom
| Hot water circulating pump fault | Rules 1, 3, 4 |  | fsbrick:Grouped_Symptom and fsbrick:hasSymptom
| Leaking mixing box damper(s) | Rules 2, 8, 10, 18 |  | fsbrick:Grouped_Symptom and fsbrick:hasSymptom
| Stuck mixing box damper(s) | Rules 2, 8, 10, 18 |  | fsbrick:Grouped_Symptom and fsbrick:hasSymptom
Taal, 2020 | AHU broken | High Co2 AND air flow rate = 0 |  | fsbrick:Grouped_Symptom and fsbrick:hasSymptom
|  | air flow rate = 0 |  | fsbrick:hasSymptom
|  | AHU air flow rate |  | fsbrick:hasSymptom
| Damper stuck | High CO2 AND air flow rate = 0 |  | fsbrick:Grouped_Symptom and fsbrick:hasSymptom
|  | High CO2 and low air flow rate |  | fsbrick:Grouped_Symptom and fsbrick:hasSymptom
|  | air flow rate = 0 |  | fsbrick:hasSymptom
|  | Low CO2 and air flow rate > 0 |  | fsbrick:Grouped_Symptom and fsbrick:hasSymptom
Zhao, 2015 | Cooling coil valve stuck (fully open) | E12, E42 | 28% | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| Cooling coil valve stuck (20% open) | E42 | 27% | fsbrick:hasSymptomProb
| Heating coil reduced capacity 1 | E42 | 99% | fsbrick:hasSymptomProb
| Heating coil reduced capacity 2 | E42 | 99% | fsbrick:hasSymptomProb
| Heating coil reduced capacity 3 | E42 | 97% | fsbrick:hasSymptomProb
| Cooling coil valve stuck (fully closed) | E12 | 67% | fsbrick:hasSymptomProb
| Cooling coil valve stuck (fully open) | E43 | 100% | fsbrick:hasSymptomProb
| Cooling coil valve stuck (partially open - 50%) | E43 | 100% | fsbrick:hasSymptomProb
| F11: Stuck heating coil (mode 1) | E33 |  | fsbrick:hasSymptom
|  | E18 |  | fsbrick:hasSymptom
|  | E42 |  | fsbrick:hasSymptom
| F12: Leaking cooling coil valve (mode 1) | E33 |  | fsbrick:hasSymptom
|  | E42 |  | fsbrick:hasSymptom
| F14: Pressure reduced on heating water circulating pump (mode 1) | E42 |  | fsbrick:hasSymptom
| F12: Leaking cooling coil valve (mode 2) | E44 |  | fsbrick:hasSymptom
|  | E12 |  | fsbrick:hasSymptom
| F21: Heating coil leaking (mode 2) | E44 |  | fsbrick:hasSymptom
|  | E12 |  | fsbrick:hasSymptom
| F26: Stuck heating coil (mode 3) | E37 |  | fsbrick:hasSymptom
|  | E43 |  | fsbrick:hasSymptom
| F21: Heating coil leaking (mode 3) | E37 |  | fsbrick:hasSymptom
|  | E43 |  | fsbrick:hasSymptom
| F22: Cooling coil tube fouling (mode 3) | E43 |  | fsbrick:hasSymptom
| F23: Chilled water circulating pump fault (mode 3) | E43 |  | fsbrick:hasSymptom
| F26: Cooling coil stuck (mode 4) | E37 |  | fsbrick:hasSymptom
|  | E43 |  | fsbrick:hasSymptom
| F22: Cooling coil tube fouling (mode 4) | E43 |  | fsbrick:hasSymptom
| F23: Chilled water circulating pump fault (mode 4) | E43 |  | fsbrick:hasSymptom
Zhao, 2017 | Exhaust air damper Stuck (fully open) | E2 (8%) |  | fsbrick:hasSymptom
| Return fan at fixed speed (30%) | E1 (2%), E2 (37%), E3 (100%) | 57% | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| Return fan complete failure | E2 (67%), E3 (100%) | 100% | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| Outdoor air damper stuck (fully closed) | E1 (5%), E2 (99%), E3 (4%) | 99% | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| AHU duct leaking (before supply fan) | E2 (90%) | 54% | fsbrick:hasSymptomProb
| AHU duct leaking (before supply fan) | E2 (79%) | 56% | fsbrick:hasSymptomProb
| Outside air damper stuck (fully closed) | E1 (100%), E2 (100%) | 79% | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| Outside air damper stuck (fully closed) | E1 (100%), E2 (100%) | 78% | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| Exhaust air damper (fully closed) | E2 (1%), E3 (100%) | 50% | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| Outside air damper stuck (fully closed) | E1 (100%), E2 (100%), E3 (51%) | 98% | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| Outside air damper stuck (40% open) | E1 (97%), E2 (100%), E3 (44%) | 93% | fsbrick:Grouped_Symptom and fsbrick:hasSymptom; fsbrick:hasSymptomProb
| Return fan complete failure | E3 (100%) | 100% | fsbrick:hasSymptomProb
| F4: OA damper stuck (mode 1) | E21 |  | fsbrick:hasSymptom
|  | E2 |  | fsbrick:hasSymptom
|  | E9 |  | fsbrick:hasSymptom
| F4: OA damper stuck (mode 2) | E12 |  | fsbrick:hasSymptom
|  | E2 |  | fsbrick:hasSymptom
|  | E9 |  | fsbrick:hasSymptom
| F5: Stuck RA damper (mode 2) | E12 |  | fsbrick:hasSymptom
|  | E20 |  | fsbrick:hasSymptom
|  | E2 |  | fsbrick:hasSymptom
|  | E3 |  | fsbrick:hasSymptom
|  | E10 |  | fsbrick:hasSymptom
| F5: Stuck RA damper (mode 3) | E20 |  | fsbrick:hasSymptom
|  | E36 |  | fsbrick:hasSymptom
|  | E2 |  | fsbrick:hasSymptom
|  | E3 |  | fsbrick:hasSymptom
|  | E10 |  | fsbrick:hasSymptom
| F5: Stuck RA damper (mode 4) | E21 |  | fsbrick:hasSymptom
|  | E2 |  | fsbrick:hasSymptom
|  | E3 |  | fsbrick:hasSymptom
|  | E10 |  | fsbrick:hasSymptom
| F6: EA damper stuck (mode 1, 2, 4) | E3 |  | fsbrick:hasSymptom
| F7: Supply fan faults (mode 1, 2, 4) | E11 |  | fsbrick:hasSymptom
|  | E1 |  | fsbrick:hasSymptom
| F8: Return fan faults (mode 1, 2, 4) | E2 |  | fsbrick:hasSymptom
|  | E3 |  | fsbrick:hasSymptom
| F9: Duct leaking before SF (mode 1, 2, 4) | E2 |  | fsbrick:hasSymptom
|  | E4 |  | fsbrick:hasSymptom
| F10: Filter faults (mode 1, 2, 4) | E4 |  | fsbrick:hasSymptom
| F4: OA damper stuck (mode 3) | E1 |  | fsbrick:hasSymptom
|  | E2 |  | fsbrick:hasSymptom
| F6: EA damper stuck | E3 |  | fsbrick:hasSymptom
| F7: Supply fan faults | E11 |  | fsbrick:hasSymptom
|  | E1 |  | fsbrick:hasSymptom
| F8: Return fan faults | E3 |  | fsbrick:hasSymptom
| F9: Leaking supply duct | E2 |  | fsbrick:hasSymptom
|  | E4 |  | fsbrick:hasSymptom
| F10: Filter fouling | E4 |  | fsbrick:hasSymptom
Liang, 2007 | recirculation damper stuck | Mixed air temperature alarm AND Outlet water temperature alarm |  | fsbrick:Grouped_Symptom and fsbrick:hasSymptom
| cooling coil fouling | Outlet water temperature alarm |  | fsbrick:hasSymptom
| cooling coil block | Outlet water temperature alarm |  | fsbrick:hasSymptom
| supply fan speed decreasing | Supply air temperature AND Outlet water temperature alarm |  | fsbrick:Grouped_Symptom and fsbrick:hasSymptom
COUNT: |  | 98 |  | 98
Goodness-of-fit percentage: |  | 100%

## Paper keys
Paper | Key
Yan, 2018 | Fault diagnosis of components and sensors in HVAC air handling systems with new types of faults
Velibeyoglu, 2019 | A graphical approach to assess the detectability of multiple simultaneous faults in air handling units
Zhu, 2019 | Novel multiblock transfer entropy based bayesian network and its application to root cause analysis
Qiu, 2020 | Modeling of HVAC systems for fault diagnosis
Pradhan, 2021 | Dynamic Bayesian Network-Based Fault Diagnosis for ASHRAE Guideline 36: High Performance Sequence of Operation for HVAC Systems
Zhao, 2017 | Diagnostic bayesian networks for diagnosing air handling units faults - part I: faults in dampers, fans, filter, and sensors
Zhao, 2015 | Diagnostic bayesian networks for diagnosing air handling units faults - part II: faults in coils and sensors
Taal, 2020 | Fault detection and diagnosis for indoor air quality in DCV systems: application of 4s3f method and effects of DBN probabilities
Yan, 2019 | Fast and Accurate Classification of Time Series Data Using Extended ELM: Application in Fault Diagnosis of Air Handling Units
Yu, 2012 | A novel methodology for knowledge discovery through mining associations between building operational data
Li, 2021 | A semi-supervised approach to fault detection and diagnosis for building HVAC systems based on the modified generative adversarial network
Fan, 2024 | Integrating active learning and semi-supervised learning for improved data-driven HVAC fault diagnosis performance
Chen, 2023 | Similarity learning-based fault detection and diagnosis in building HVAC systems with limited labeled data
House, APAR | An expert rule set for fault detection in Air-Handling Units
Liang, 2007 | Model-based fault detection and diagnosis of HVAC systems using support vector machine method
**for component faults only