## Fault Mapping
Paper | Faults | Fault Mapping to FSBrick |  | FSBrick Entities | Count for FSBrick
Yan, 2018 | cooling coil tube fouling | Cooling_Coil_Fouling |  | Cooling_Coil_Fouling | 2
| cooling coil dust on fins |  | no controlled vocab for this fault nature | Cooling_Valve_Stuck | 6
| cooling coil valve stuck closed | Cooling_Valve_Stuck |  | Damper_Stuck | 2
| cooling coil valve stuck open | Cooling_Valve_Stuck |  | Water_Valve_Stuck | 1
Qiu, 2020 | air valve stuck (of specific room) | Damper_Stuck |  | Fan_Stuck | 1
| water valve stuck | Water_Valve_Stuck |  | Pump_Stuck | 1
| fan stuck | Fan_Stuck |  | Coil_Fouling | 1
| pump stuck | Pump_Stuck |  | Outside_Damper_Stuck | 4
| pipe scaling | Coil_Fouling |  | Return_Fan_Malfunctioning | 4
Pradhan, 2021 | AHU outdoor air damper stuck higher than normal | Outside_Damper_Stuck |  | Outside_Damper_Leakage | 2
| AHU outdoor air damper stuck lower than normal | Outside_Damper_Stuck |  | Supply_Air_Plenum_Leakage | 2
| AHU cooling coil valve stuck higher than normal | Cooling_Valve_Stuck |  | Return_Damper_Stuck | 1
| AHU cooling coil valve stuck lower than normal | Cooling_Valve_Stuck |  | Exhaust_Damper_Stuck | 2
| AHU return fan speed higher than normal | Return_Fan_Malfunctioning |  | Supply_Fan_Stuck | 1
| AHU return fan speed lower than normal | Return_Fan_Malfunctioning |  | Return_Fan_Stuck | 2
| AHU return fan complete failure | Return_Fan_Malfunctioning |  | Filter_Block | 3
| AHU outdoor air damper leaking | Outside_Damper_Leakage |  | Heating_Valve_Stuck | 1
| AHU air loop supply duct leakage | Supply_Air_Plenum_Leakage |  | Heating_Coil_Fouling | 2
Zhao, 2017 | Stuck OA damper | Outside_Damper_Stuck |  | Heating_Valve_Leakage | 1
| Stuck RA damper | Return_Damper_Stuck |  | Supply_Fan_Malfunctioning | 1
| Stuck EA damper | Exhaust_Damper_Stuck |  | Damper_Malfunctioning | 1
| Stuck supply air fan | Supply_Fan_Stuck |  | Air_Plenum_Leakage | 1
| Stuck return air fan | Return_Fan_Stuck |  | Air_Plenum_Block | 1
| Leaking supply duct | Supply_Air_Plenum_Leakage |  | Mixed_Damper_Malfunctioning | 1
| Filter fouling | Filter_Block
Zhao, 2015 | Stuck heating coil | Heating_Valve_Stuck
| Leaking cooling coil valve | Cooling_Valve_Leakage
| Heating coil fouling | Heating_Coil_Fouling
| Pressure reduced on heating water circulating pump |  | pressure should be reduced by something; Therefore, this is a 'symptom' by our definition
| Leaking heating coil valve | Heating_Valve_Leakage
| Cooling coil fouling | Cooling_Coil_Fouling
| Pressure reduced on chilled water circulating pump |  | pressure should be reduced by something; Therefore, this is a 'symptom' by our definition
| Stuck cooling coil | Cooling_Valve_Stuck
Taal, 2020 | Supply fan broken | Supply_Fan_Malfunctioning
| Return fan broken | Return_Fan_Malfunctioning
| Damper is broken | Damper_Malfunctioning
| Bad filter | Filter_Block
| Leaking ducts | Air_Plenum_Leakage
| Clogged ducts | Air_Plenum_Block
| Stuck damper (room damper is broken) | Damper_Stuck
Yan, 2019 | EA damper stuck | Exhaust_Damper_Stuck
| Return fan stuck | Return_Fan_Stuck
| Cooling coil valve stuck | Cooling_Valve_Stuck
| Outdoor air damper stuck | Outside_Damper_Stuck
| OA damper leak | Outside_Damper_Leakage
| AHU duct leaking before supply fan |  | Duct is not a term in Brick
| AHU duct leaking after supply fan |  | Duct is not a term in Brick
| Air filter blocked | Filter_Block
| Mixed air damper unstable | Mixed_Damper_Malfunctioning
| Heating coil fouling | Heating_Coil_Fouling
| Heating coil reduced capacity |  | heating coil should have reduced capacity by something; Therefore, this is a 'symptom' by our definition
Count: | 51 | 45
Goodness-of-fit percentage: | 0.88235

## Fault Severity Mapping
Paper | Faults | Severity | Fault Mapping to FSBrick |  | FSBrick Entities | Count for FSBrick
Yan, 2018 | cooling coil tube fouling | decrease in tube diameter | hasSeverity; brick:Flow with value Literal |  | hasSeverity; brick:Flow with value Literal | 16
| cooling coil dust on fins | decrease in surface area |  |  | hasSeverity; brick:Position with value Literal | 38
| cooling coil valve stuck closed | 0% | hasSeverity; brick:Position with value Literal |  | hasSeverity; brick:Rotational_Speed with value Literal | 9
| cooling coil valve stuck open | 100% | hasSeverity; brick:Position with value Literal
Qiu, 2020 | air valve stuck (of specific room) | 80% open | hasSeverity; brick:Position with value Literal
water valve stuck
fan stuck
pump stuck
| pipe scaling | 75% | hasSeverity; brick:Flow with value Literal
Pradhan, 2021 | AHU outdoor air damper stuck higher than normal | 10% | hasSeverity; brick:Position with value Literal
|  | 0% | hasSeverity; brick:Position with value Literal
|  | 100% | hasSeverity; brick:Position with value Literal
|  | 15% | hasSeverity; brick:Position with value Literal
|  | 5% | hasSeverity; brick:Position with value Literal
AHU outdoor air damper stuck lower than normal
| AHU cooling coil valve stuck higher than normal | 0% (100% is in here too, but it is a duplicate of c5) | hasSeverity; brick:Position with value Literal
|  | 15% | hasSeverity; brick:Position with value Literal
|  | 5% | hasSeverity; brick:Position with value Literal
AHU cooling coil valve stuck lower than normal
AHU return fan speed higher than normal
AHU return fan speed lower than normal
AHU return fan complete failure
AHU outdoor air damper leaking
| AHU air loop supply duct leakage | 20% | hasSeverity; brickFlow with value Literal
Zhao, 2017 | Stuck OA damper | max position | hasSeverity; brick:Position with value Literal
|  | partially open | hasSeverity; brick:Position with value Literal
|  | min position | hasSeverity; brick:Position with value Literal
| Stuck RA damper | max position | hasSeverity; brick:Position with value Literal
|  | partially open | hasSeverity; brick:Position with value Literal
|  | min position | hasSeverity; brick:Position with value Literal
| Stuck EA damper | max position | hasSeverity; brick:Position with value Literal
|  | partially open | hasSeverity; brick:Position with value Literal
|  | min position | hasSeverity; brick:Position with value Literal
| Stuck supply air fan | max speed | hasSeverity; brick:Rotational_Speed with value Literal
|  | min speed | hasSeverity; brick:Rotational_Speed with value Literal
|  | partial speed | hasSeverity; brick:Rotational_Speed with value Literal
|  | complete failure |  | difficulty with qualitative descriptors
| Stuck return air fan | max speed | hasSeverity; brick:Rotational_Speed with value Literal
|  | min speed | hasSeverity; brick:Rotational_Speed with value Literal
|  | partial speed | hasSeverity; brick:Rotational_Speed with value Literal
|  | complete failure |  | difficulty with qualitative descriptors
| Leaking supply duct | heavily | hasSeverity; brick:Flow with value Literal
|  | slightly | hasSeverity; brick:Flow with value Literal
| Filter fouling | fouling | hasSeverity; brick:Flow with value Literal
|  | broken |  | difficulty with qualitative descriptors
Zhao, 2015 | Stuck heating coil | stuck at max | hasSeverity; brick:Position with value Literal
|  | positive |  | difficulty with qualitative descriptors
|  | negative |  | difficulty with qualitative descriptors
|  | stuck at min | hasSeverity; brick:Position with value Literal
| Leaking cooling coil valve | leaking heavily | hasSeverity; brick:Flow with value Literal
|  | leaking slightly | hasSeverity; brick:Flow with value Literal
Heating coil fouling
Pressure reduced on heating water circulating pump
| Leaking heating coil valve | leaking heavily | hasSeverity; brick:Flow with value Literal
|  | leaking slightly | hasSeverity; brick:Flow with value Literal
Cooling coil fouling
Pressure reduced on chilled water circulating pump
| Stuck cooling coil | stuck at max | hasSeverity; brick:Position with value Literal
|  | positive stuck |  | difficulty with qualitative descriptors
|  | negative stuck |  | difficulty with qualitative descriptors
|  | stuck at min | hasSeverity; brick:Position with value Literal
Taal, 2020 | Supply fan broken
Return fan broken
Damper is broken
Bad filter
Leaking ducts
Clogged ducts
Stuck damper (room damper is broken)
Yan, 2019 | EA damper stuck | fully open | hasSeverity; brick:Position with value Literal
|  | fully closed | hasSeverity; brick:Position with value Literal
|  | 40% open | hasSeverity; brick:Position with value Literal
| Return fan stuck | 30% speed | hasSeverity; brick:Rotational_Speed with value Literal
|  | 20% speed | hasSeverity; brick:Rotational_Speed with value Literal
|  | 80% speed | hasSeverity; brick:Rotational_Speed with value Literal
|  | complete failure |  | difficulty with qualitative descriptors
| Cooling coil valve stuck | fully closed | hasSeverity; brick:Position with value Literal
|  | fully open | hasSeverity; brick:Position with value Literal
|  | 15% partially open | hasSeverity; brick:Position with value Literal
|  | 65% partially open | hasSeverity; brick:Position with value Literal
|  | 50% partially open | hasSeverity; brick:Position with value Literal
| Outdoor air damper stuck | fully closed | hasSeverity; brick:Position with value Literal
| OA damper leak | 55% open | hasSeverity; brick:Position with value Literal
|  | fully closed | hasSeverity; brick:Position with value Literal
AHU duct leaking before supply fan
AHU duct leaking after supply fan
| Air filter blocked | 10% of area | hasSeverity; brick:Flow with value Literal
|  | 25% of area | hasSeverity; brick:Flow with value Literal
Mixed air damper unstable
| OA damper stuck | fully closed | hasSeverity; brick:Position with value Literal
| OA damper leaking | 52% open | hasSeverity; brick:Position with value Literal
|  | 62% open | hasSeverity; brick:Position with value Literal
| Heating coil fouling | stage 1 | hasSeverity; brick:Flow with value Literal
|  | stage 2 | hasSeverity; brick:Flow with value Literal
| Heating coil reduced capacity | stage 1 | hasSeverity; brick:Flow with value Literal
|  | stage 2 | hasSeverity; brick:Flow with value Literal
|  | stage 3 | hasSeverity; brick:Flow with value Literal
COUNT: |  | 73 | 64
Goodness-of-fit percentage: |  | 0.87671

## Symptom Mapping
Paper | Symptoms | Fault Mapping to FSBrick | Alarm | Medium & measurement alarm
Yan, 2018 | outdoor air temperature | hasSymptom; brick:Air_Temperature_Alarm; (brick:Outside_Air) | TRUE | TRUE
| supply air temperature | hasSymptom; brick:Supply_Air_Temperature_Alarm | TRUE | TRUE
| return air temperature | hasSymptom; brick:Return_Air_Temperature_Alarm | TRUE | TRUE
| outdoor air humidity | hasSymptom; brick:Humidity_Alarm; (brick:Outside_Air) | TRUE | TRUE
| supply air humidity | hasSymptom; brick:Humidity_Alarm; (brick:Supply_Air) | TRUE | TRUE
| return air humidity | hasSymptom; brick:Humidity_Alarm; (brick:Return_Air) | TRUE | TRUE
| outdoor air mass flow rate | hasSymptom; brick:Air_Flow_Alarm; (brick:Outside_Air) | TRUE | TRUE
| supply air mass flow rate | hasSymptom; brick:Air_Flow_Alarm; (brick:Supply_Air) | TRUE | TRUE
| return air mass flow rate | hasSymptom; brick:Air_Flow_Alarm; (brick: Return_Air) | TRUE | TRUE
| chilled water temperature | hasSymptom; brick:Water_Temperature_Alarm; (brick:Chilled_Water) | TRUE | TRUE
| chilled water mass flow rate | (brick:Chilled_Water) | TRUE | FALSE
| supply fan power consumption | hasSymptom; brick:Power_Alarm; (brick:Supply_Fan) | TRUE | TRUE
| return fan power consumption | hasSymptom; brick:Power_Alarm; (brick:Return_Fan) | TRUE | TRUE
Qiu, 2020 | low room air temperature (&increased fan energy consumption, increased water pump energy consumption) | hasSymptom; brick:Air_Temperature_Alarm; (brick:Zone_Air) | TRUE | TRUE
| increased fan energy consumption | hasSymptom; brick:Power_Alarm; (brick:Fan) | TRUE | TRUE
| increased water pump energy consumption | hasSymptom; brick:Power_Alarm; (brick:Water_Pump) | TRUE | TRUE
|  |  | FALSE | FALSE
| supply air temperature alarm (increased fan energy consumption, increased water pump energy consumption) | hasSymptom; brick:Supply_Air_Temperature_Alarm | TRUE | TRUE
Zhao, 2017 | Difference between supply air pressure and its set point (positive) | hasSymptom; brick:Pressure_Alarm; (brick:Supply_Air) | TRUE | TRUE
| Difference between supply air pressure and its set point (negative) | hasSymptom; brick:Pressure_Alarm; (brick:Supply_Air) | TRUE | TRUE
| Supply fan power consumption is a polynomial function of supply air flow rate (extremely positive) | hasSymptom; brick:Power_Alarm; (brick:Supply_Fan) | FALSE | FALSE
| Supply fan power consumption is a polynomial function of supply air flow rate (positive) | hasSymptom; brick:Power_Alarm; (brick:Supply_Fan) | FALSE | FALSE
| Supply fan power consumption is a polynomial function of supply air flow rate (negative) | hasSymptom; brick:Power_Alarm; (brick:Supply_Fan) | FALSE | FALSE
| Return fan power consumption is a polynomial function of return fan speed (positive) | hasSymptom; brick:Power_Alarm; (brick:Return_Fan) | FALSE | FALSE
| Return fan power consumption is a polynomial function of return fan speed (negative) | hasSymptom; brick:Power_Alarm; (brick:Return_Fan) | FALSE | FALSE
| Pressure drop across a filter is a polynomial function of supply air flow rate (positive) | hasSymptom; brick:Pressure_Alarm; (brick:Filter) | FALSE | FALSE
| Pressure drop across a filter is a polynomial function of supply air flow rate (negative) | hasSymptom; brick:Pressure_Alarm; (brick:Filter) | FALSE | FALSE
| Pressure drop across a filter is a polynomial function of supply air flow rate (zero) | hasSymptom; brick:Pressure_Alarm; (brick:Filter) | FALSE | FALSE
| Difference between return air and mixed air temperatures (negative) | hasSymptom; brick:Air_Temperature_Alarm; | FALSE | FALSE
| Difference between return air and mixed air temperatures (positive) | hasSymptom; brick:Air_Temperature_Alarm; | FALSE | FALSE
| Difference between outdoor air and mixed air temperatures (negative) | hasSymptom; brick:Air_Temperature_Alarm; | FALSE | FALSE
| Difference between outdoor air and mixed air temperatures (positive) | hasSymptom; brick:Air_Temperature_Alarm; | FALSE | FALSE
| Supply fan power measurement (max value) | hasSymptom; brick:Power_Alarm | TRUE | TRUE
| Supply fan power measurement (min value) | hasSymptom; brick:Power_Alarm | TRUE | TRUE
| Supply fan power measurement (partial value) | hasSymptom; brick:Power_Alarm | TRUE | TRUE
| Supply fan power measurement (zero) | hasSymptom; brick:Power_Alarm | TRUE | TRUE
| F_sa - F_ra | hasSymptom; brick:Air_Flow_Alarm; | FALSE | FALSE
| Delta pressure filter reading over the past x hours (frozen) | hasSymptom; brick:Pressure_Alarm; (brick:Filter) | TRUE | TRUE
| Delta pressure filter reading over the past x hours (not frozen) | hasSymptom; brick:Pressure_Alarm; (brick:Filter) | TRUE | TRUE
|  |  | FALSE | FALSE
| R2 and R18 in APAR (present) |  | FALSE | FALSE
| R27 in APAR (present) | (brick:Mixed_Air_Temperature) | TRUE | FALSE
| R10 in APAR (present) |  | FALSE | FALSE
Zhao, 2015 | Supply air temperature is too low | hasSymptom; brick:Supply_Air_Temperature_Alarm | TRUE | TRUE
| Cooling coil control signal open valve | hasSymptom; brick:Valve_Position_Alarm; (brick:Cooling_Valve) | TRUE | TRUE
| Cooling coil control signal close valve | hasSymptom; brick:Valve_Position_Alarm; (brick:Cooling_Valve) | TRUE | TRUE
| Predicted control signal of heating coil valve vs actual value (positive max) | hasSymptom; brick:Valve_Position_Alarm; (brick:Heating_Valve) | TRUE | TRUE
| Predicted control signal of heating coil valve vs actual value (positive) | hasSymptom; brick:Valve_Position_Alarm; (brick:Heating_Valve) | TRUE | TRUE
| Predicted control signal of heating coil valve vs actual value (negative) | hasSymptom; brick:Valve_Position_Alarm; (brick:Heating_Valve) | TRUE | TRUE
| Predicted control signal of heating coil valve vs actual value (negative min) | hasSymptom; brick:Valve_Position_Alarm; (brick:Heating_Valve) | TRUE | TRUE
| Status of chilled water circulating pump (closed) | (brick:Chilled_Water_Pump) brick:Position_Alarm | TRUE | TRUE
| Reduced pressure of pressure difference of the supply heating water loop | hasSymptom; brick:Pressure_Alarm; (brick:Hot_Water_Pump) | TRUE | TRUE
| Low temperature of supply heating water | hasSymptom; brick:Water_Temperature_Alarm; (brick:Supply_Hot_Water) | TRUE | TRUE
| R7 in APAR Positive | (brick:Supply_Air_Temperature) | TRUE | FALSE
| R7 in APAR negative | (brick:Supply_Air_Temperature) | TRUE | FALSE
| Supply air temperature outside of threshold (lo) | hasSymptom; brick:Supply_Air_Temperature_Alarm | TRUE | TRUE
| Supply air temperature outside of threshold (hi) | hasSymptom; brick:Supply_Air_Temperature_Alarm | TRUE | TRUE
| Closed heating water circulating pump | (brick:Hot_Water_Pump); brick:Position_Alarm | TRUE | TRUE
| Supply air temperature too high | hasSymptom; brick:Supply_Air_Temperature_Alarm | TRUE | TRUE
| Predicted control signal of cooling coil valve vs actual value (positive max) | hasSymptom; brick:Valve_Position_Alarm; (brick:Cooling_Valve) | TRUE | TRUE
| Predicted control signal of cooling coil valve vs actual value (positive) | hasSymptom; brick:Valve_Position_Alarm; (brick:Cooling_Valve) | TRUE | TRUE
| Predicted control signal of cooling coil valve vs actual value (negative) | hasSymptom; brick:Valve_Position_Alarm; (brick:Cooling_Valve) | TRUE | TRUE
| Predicted control signal of cooling coil valve vs actual value (negative min) | hasSymptom; brick:Valve_Position_Alarm; (brick:Cooling_Valve) | TRUE | TRUE
| High supply chilled water temperature | hasSymptom; brick:Water_Temperature_Alarm (brick:Supply_Chilled_Water) | TRUE | TRUE
Taal, 2020 | AHU flow rate = 0 (AHU flow rate = 0 OR flow rate = 0 and occupied OR High CO2 and flow rate = 0) | hasSymptom; brick:Air_Flow_Alarm; (brick:AHU) | TRUE | TRUE
| CO2 (High CO2 and flow rate = 0 OR High CO2 and low flow rate OR low CO2 and non zero flow rate; occupied but flow rate is zero) | hasSymptom; brick:CO2_Alarm; (brick:AHU) | TRUE | TRUE
Yan, 2019 | Energy Consumption of cooling coil | hasSymptom; brick:Power_Alarm; (brick:Cooling_Coil) | TRUE | TRUE
| Energy consumption of heating coil | hasSymptom; brick:Power_Alarm; (brick:Heating_Coil) | TRUE | TRUE
| Supply air temperature | hasSymptom; brick:Supply_Air_Temperature_Alarm | TRUE | TRUE
| Return air temperature | hasSymptom; brick:Return_Air_Temperature_Alarm | TRUE | TRUE
| Supply air relative humidity | hasSymptom; brick:Humidity_Alarm; (brick:Supply_Air) | TRUE | TRUE
COUNT: | 69 |  |  | 50
Goodness-of-fit percentage: |  |  |  | 0.72464

## Paper keys
Paper | Key
Yan, 2018 | Fault diagnosis of components and sensors in HVAC air handling systems with new types of faults
Velibeyoglu, 2019 | A graphical approach to assess the detectability of multiple simultaneous faults in air handling units
Zhu, 2019 | Novel multiblock transfer entropy based bayesian network and its application to root cause analysis
Qiu, 2020 | Modeling of HVAC systems for fault diagnosis
Pradhan, 2021 | Dynamic Bayesian Network-Based Fault Diagnosis for ASHRAE Guideline 36: High Performance Sequence of Operation for HVAC Systems
Zhao, 2017 | Diagnostic bayesian networks for diagnosing air handling units faults - part I: faults in dampers, fans, filter, and sensors
Zhao, 2015 | Diagnostic bayesian networks for diagnosing air handling units faults - part II: faults in coils and sensors
Taal, 2020 | Fault detection and diagnosis for indoor air quality in DCV systems: application of 4s3f method and effects of DBN probabilities
Yan, 2019 | Fast and Accurate Classification of Time Series Data Using Extended ELM: Application in Fault Diagnosis of Air Handling Units
**for component faults only